Section 13081

Sound Control window Systems

STC 57, noise-lock windows

# Part 1 - General

1.01	 SUMMARY

A. 	Provide sound control window assemblies where shown on the Drawings, as specified herein, and listed on the Window Schedule.  The work includes window assemblies complete with frames, stops, glazing, sound-absorbing material and concealed fasteners factory installed. Glass and glazing material are factory assembled in frame and shipped complete as one unit.

B.	Related Sections:

1.	Section 04200:  Concrete Unit Masonry.

2.	Section 08810:  Glazing

3.	Section 09110:  Metal Stud System.

4.	Section 09260:  Gypsum Wallboard System.

5.	Section 09900:  Painting.

1.02	SYSTEM PERFORMANCE REQUIREMENTS

- Sound Rating:  Provide window assemblies that have been fabricated as sound-retardant units, tested according to ASTM E 90 and have the following certified Sound Transmission Class (STC) rating as determined according to ASTM E 413.

  - STC Rating 57

1.03	SUBMITTALS

A.	Comply with pertinent provisions of the Contract and Division 1.

B.	Product Data:  Within 30 calendar days after the Contractor has received the Owner’s Notice to Proceed, submit:

1.	Material lists of items provided under this Section.

2.	Manufacturer’s specifications and other data needed to prove 				compliance with the specified requirements.

3.	Shop Drawings showing details of each frame type, elevations of door designs, details of openings, and details of construction, installation and anchorage.

4.	Manufacturer’s recommended installation procedures which, when 			approved by the Architect, will become the basis for accepting or 				rejecting actual installation procedures used on the work.

5.	Test Reports from a qualified independent testing agency indicating and interpreting test results from Part 3 of this Section relative to compliance of sound ratings with the indicated requirements.

DELETE BELOW IF NOT ALLOWED.

6.	Material certificates in lieu of laboratory test reports when permitted by Architect signed by the manufacturer certifying that each sound control window complies with the project requirements.

DELETE BELOW UNLESS FIELD TESTING SERVICES ARE PART OF CONTRACT.

7.	Field test reports from qualified independent testing agency indicating and interpreting test results relative to compliance with performance requirements of installed sound control windows.

1.04	QUALITY ASSURANCE

A.	Use adequate numbers of skilled workmen who are thoroughly trained 			and experienced in the necessary crafts and who are completely familiar 			with the specified requirements and the methods needed for proper 			performance of the work of this Section.

B.	Acoustical Performance

1.	The acoustical window manufacturer will be required to submit 				acoustical performance data in the form of up-to-date test reports

from an independent testing laboratory indicating the windows to be provided will have the required Sound Transmission Class Rating (ASTM E-90-90).

2.	For the required STC rating, refer to window schedule drawing.

3.	Owner may at his option order performance tests of installed window assemblies by an independent consultant to verify compliance with the specifications.  Any discrepancies shall be repaired or replaced without cost to the Owner.

C.	Single-Source Responsibility:  Provide sound control windows, including stops, glazing, frame and sound-absorbing material essential for sound control as an assembly and by a single firm specializing in producing this type of work for a minimum of ten (10) years.

1.05	DELIVERY, STORAGE AND HANDLING

A.	Use all means necessary to protect the materials of this section 				before,	during and after installation and to protect the installed 				work and materials of all other trades.

1.06	WARRANTY

A.	Acoustic window materials and associated hardware shall be guaranteed against defective workmanship for one (1) year from date of shipment.

Part 2 - Products

2.01	MANUFACTURERS

A.	Provide double glazed, “Noise Lock” acoustic window(s) and frame(s) with stops, glazing, sound-absorbing material, and concealed fasteners as manufactured by IAC Acoustics, North Aurora, IL.
Contact: Tim O’Neill of O’Neill Engineered Systems.  262-367-6700 phone toneill@noiseproblems.com e-mail. Equivalent products will be considered, when submitted for approval prior to the bid opening, and meet or exceed the requirements of this specification.

2.02	MANUFACTURED ASSEMBLIES (NOISE LOCK WINDOWS)

- Glass pane(s) minimum thickness:

STC 57 Rating, ½” (13 mm) interior, ¼” (6 mm) exterior – double pane

Glass type shall be:  ¼” Laminated Safety Glass & ½” Laminated Safety Glass

B.	Frame(s) shall be 1 ¼” thick, fabricated from not less than 12 gauge cold rolled, galvannealed steel with an A60 coating weight, reinforced and filled with sound-absorbing acoustic fill.  Inside and outside corners shall be mitered and interlocked to hairline measurements, made square, continuously welded, and ground smooth, flush and invisible.  The window assembly can be installed into either existing or new construction openings.

C.	Acoustic seals for glazing shall be vibration-isolating resilient gaskets, U-shaped and continuous santoprene UV grade 65-75 durometer black.  Self-contained, sound absorptive interior perimeter of not less than 22 gauge (0.76 mm) steel shall be perforated and pre-finished black.  Desiccant material shall be incorporated into multiple glazed units.

D.	Stops:  Provide stops that are 1” (25 mm) high (min) and readily removable, fabricated from not less than 16 gauge (2 mm) rolled steel sections predrilled and aligned with frame to form tight square acoustical joints.  Stop fasteners shall be concealed.

E.	Assembly:  The assembly of the acoustic window units including frames, stops, glazing, acoustic seals, sound-absorbing material and concealed fasteners shall take place at the factory to insure required noise reduction is achieved.  Glazing shall not need to be removed to facilitate fastening or anchoring at the job site.

2.03	FABRICATION

A.	General:  Fabricate units to be rigid, neat in appearance and free from defects, warp or buckle.  Accurately form metal to required sizes and profiles.  Wherever practical, fit and assemble units in the manufacturer’s plant.  Identify work that is not permanently factory-assembled before shipment to ensure proper assembly at the Project site.  Weld exposed joints continuously:  grind, fill dress and make smooth flush and invisible.

2.04	FINISHES (FACTORY)

- Frames shall receive a shop coat of a rust-inhibitive primer.  The primer shall be applied over properly prepared metal, in accordance with the manufacturer’s standard shop prime coat procedure and oven-baked dry.

- Others, as required, will perform finish painting, under the painting section 0990 of this Specification.

#### PART 3 - EXECUTION

  - MANUFACTURER’S INSTRUCTIONS

- Compliance:  Comply with manufacturer’s product data, including product technical bulletins, product catalog installation instructions and product carton instructions.

  - PREPARATION

- Adjacent Surfaces Protection:  Protest adjacent work areas and finish surfaces from damage during product installation.

- Adjacent Construction:  Coordinate window assembly details with details of adjacent work to ensure proper attachments and clean junctions.

  - INSTALLATION

- Install work in accordance with reviewed shop drawings and these specifications using only factory-trained personnel as required by the Manufacturer and approved by the Architect.

  - Install windows and shim accordingly to allow for a plumb and square installation without excessive clearances.

  - During installation, solidly pack acoustic insulation around frames that are installed in stud and gypsum-wallboard partitions.

  - Caulk exterior joint prior to painting.

  - Install sound control window assemblies during finish phase of construction to protect units from damage.

  - FIELD QUALITY CONTROL

- Upon completion of this portion of work, and prior to its acceptance by the Owner, secure a visit to the job site by a qualified representative of the manufacturer of the acoustical door system(s) to confirm that installation is in conformance with the manufacturer’s recommendations.

3.05	FIELD TESTING

- Testing Agency:  Owner will employ and pay an independent testing agency to perform sound control field testing.

DELETE ABOVE OR BELOW.  RETAIN BELOW IF FIELD TESTING SERVICES ARE PART OF CONTRACT.

- Testing Agency:  Provide the service of an independent testing agency experienced in testing sound control windows and is acceptable to architect to perform sound control field-testing.

- Selection:  Randomly selected by Owner, except not-completely installed sound windows.

- Testing Requirements:  Conduct field tests according to ASTM E336 with results calculated according to ASTM E413 to confirm that the operating field NIC values are within 5 dB of laboratory STC values.

- Test results shall be reported promptly and in writing by testing agency to Owner, Contractor and Architect.

- Repair or replace components of sound control windows where test results indicate STC rating does not meet requirements.

3.06	DEMONSTRATION

- Instruct the Owner’s maintenance personnel regarding the maintenance of all acoustic windows.

END OF SECTION